## Information and Instructions
RFP Questions and Requirements
This document contains multiple sections of questions and standard requirements that are broken down into categories, separated by worksheets, and based on areas of focus. Some categories contains sub-sections for a more granular look at required vendor capabilities. These requirements are meant to exhibit capability, functionality, and flexibility across the entire DERMS implementation. This information will be used in the evaluation of the RFP response. Respondents are asked to provide information to illustrate if the itemized functionality is in the current DERMS product, part of the existing DERMS vendor roadmap, if the system would require additional custom development and investment, or not in scope for the DERMS system.
Each requirement must be addressed in the vendor response section (highlighted GREY on the right of the page). Please indicate your response with an "X" in the category that best describes your system's abilities. There is a section for notes and additional information to clarify your response.

## DER Integration
ID | Requirement | Use Case Description | Vendor Response Section
| Integration |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
INT-1 | DERMS shall pass market signals to another head-end system | In support of market participation, taking market signals from the wholesale market and creating events for head-end systems under DERMS control
INT-2 | DERMS shall have the ability to integrate with a 3rd party weather forecasting service for consumption of weather forecast data | To enhance solar production forecasts, as well as inform future flexibility forecasts based on weather conditions impacts on previous events
INT-3 | DERMS shall have the ability to integrate with a 3rd party solar irradiance forecasting service for consumption of solar irradiance data | To enhance solar production forecasts, as well as inform future flexibility forecasts based on weather conditions impacts on previous events
INT-4 | DERMS shall support EV charging integrations | In support of DSM programs and commercial EV charging programs
INT-5 | DERMS shall support EV OEM integrations for telematics | In support of DSM programs and commercial EV battery control programs
INT-6 | DERMS shall support V2G integration | Utilizing EV chargers for grid support and market participation
INT-7 | DERMS shall support integrations with 3rd party distributed generation head-end systems | In support of DSM programs
INT-8 | DERMS shall have the capability to integrate with 3rd party systems through SOAP and RESTful web services | Standard web services protocols
INT-9 | DERMS shall receive external event dispatch signals and create subsequent events for directly connected assets and DER head-end systems | External signals may come from internal systems to dispatch DSM program head-ends
INT-10 | DERMS shall support integration with utility CIS | In support of all program management
INT-11 | DERMS shall support integration with PI data historian | In support of all program management and EM&V efforts
INT-12 | DERMS shall support non-telemetered resources (i.e. manual upload and management of data) | To ensure existing utility assets can be included in the DERMS

## DER Registration
ID | Requirement | Use Case Description | Vendor Response Section
| Registration |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
REG-1 | DERMS shall support the configuration of the following data in the system: | Key data to identify customers across utility systems
Account number
Account type (residential, commercial, industrial)
Meter ID
Rate Category
Program Enrollments
Name
Address
Email
Premise ID
| Network location identifier(s) | In support of grouping assets based on network location, i.e. substation, transformer, line segment, etc.
REG-2 | DERMS shall be able to identify and configure individual FTM and BTM assets | In support of locational grid support by DER assets, program participation in DSM, and locational distribution programs
REG-3 | DERMS shall support asset aggregations (same or different technology types) | In support of locational grid support by DER assets, program participation in FERC 2222, and locational distribution programs
REG-4 | DERMS shall allow a single customer to have multiple assets | In support of single customers owning multiple asset types participating in different DSM programs
REG-5 | DERMS shall allow a single meter to be associated with multiple assets | In support of single customers owning multiple asset types participating in different DSM programs
REG-6 | DERMS shall automatically update customer and asset meters (i.e. when meter changes occur) | When customer information changes in the system of record (i.e. meter exchange, rate class change), changes shall be reflected in DERMS
REG-7 | DERMS shall allow single assets to be included in multiple groupings | This data field tracks DER interconnection requirements
REG-8 | DERMS shall allow customers to enroll in multiple programs (if program parameters allow) | DSM customers may participate in multiple programs with either single assets or multiple assets
REG-9 | DERMS shall support non-telemetered resources (i.e. manual upload and management of data) | To ensure all existing devices can be incorporated into the DERMS
REG-10 | DERMS shall import nameplate data from individual and aggregated DERs | This data field tracks DER interconnection requirements
REG-11 | DERMS shall import operating power factor limits for individual DERs | This data field supports DER advanced inverter functionality
REG-12 | DERMS shall import ramp rates for individual or aggregated DERs | This data field tracks DER interconnection requirements
REG-13 | DERMS shall import charging and discharging limitations for individual or aggregated DERs | This data field tracks DER interconnection requirements
| Topology |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
REG-14 | DERMS shall have the capability to aggregate assets from multiple vendors and technologies into a VPP based on locational information | Multiple vendors and asset-types can be grouped into single groups when delivering locational grid support
REG-15 | DERMS shall allow for the real-time monitoring of individual or aggregated loads on specific circuits | In support of distribution operations and distribution planning

## Security and Architecture
ID | Requirement | Vendor Response Section
| Cyber Security | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
SEC-1 | DERMS vendor organization shall implement processes designed to ensure all of your network connections and devices are adequately tracked, managed, and controlled to protect against threats and to maintain security for the systems and applications using the network
SEC-2 | DERMS shall support role-based access control (RBAC) for end-users
SEC-3 | DERMS shall support role-based access control (RBAC) for system administrators
SEC-4 | DERMS shall support integration with Enterprise LDAP/Active Directory to perform RBAC and Authentication
SEC-5 | DERMS vendor shall identify which type of access requires multi-factor authentication (e.g., any access, remote access, admin access, etc.) and ensure support of MFA via Active Directory through Office 365
SEC-6 | DERMS shall digitally sign and validate software, patches, and firmware prior to distribution
SEC-7 | DERMS vendor organization shall have a data privacy policy that applies to your computing systems
SEC-8 | DERMS vendor shall maintain a defined problem escalation plan in your BCP for impacted clients of the computing system
SEC-9 | DERMS shall have a disaster recovery plan (DRP) for your computing systems
SEC-10 | DERMS shall have data retention policies that are relevant to this engagement
SEC-11 | Utility shall retain ownership rights to all data, inputs, outputs, and metadata
SEC-12 | Procedures shall exist to ensure that retention and destruction of data meets established business and regulatory requirements
SEC-13 | If project implementation team shall require offshore resources, specify in which countries they are located
SEC-14 | If your development work include offshore resources, specify in which countries are they located
| Architecture | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
SEC-15 | If your system is SaaS, your organization shall maintain privacy of the utility data from other utilities
SEC-16 | Audit logs shall be available for all changes to the network, firewall, IDS, and IPS systems
SEC-17 | Audit logs shall be available for all attempted logins and logged in user activity
SEC-18 | Specify if any of your servers reside in a co-located data center
SEC-19 | Your organization shall accommodate encryption requirements using open standards
SEC-20 | DERMS shall have the ability to be hosted in the cloud
SEC-23 | DERMS shall support multi-site or other forms of redundancy
SEC-24 | DERMS shall have controls for preventing and responding to denial of service (DOS) and distributed denial of service (DDoS) attacks
SEC-25 | DERMS shall have controls for preventing and responding to injection attacks and cross site scripting
SEC-26 | DERMS shall support integration with log aggregation and monitoring services
| Data Protection | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
SEC-27 | Specify whether any utility data will be stored in the cloud
SEC-28 | DERMS shall have a documented program to identify, classify, protect, manage, and maintain sensitive information
SEC-29 | Information protection program shall prohibit access to customer data without authorization
SEC-30 | Your platform shall implement process and controls to ensure system and information integrity
SEC-31 | Specify whether the utility's data will be stored on any devices (database servers, file servers, SAN, NAS, etc.) configured with non-RFC 1918/4193 (i.e., publicly routable) IP addresses
SEC-32 | Structured databases shall be encrypted
SEC-33 | Unstructured utility data (e.g., file shares) shall be encrypted
SEC-34 | DERMS shall employ encryption technologies (e.g., SSH, SSL/TLS, VPN) when transmitting sensitive information
SEC-35 | DERMS shall employ encryption technologies to secure data at rest (e.g., configuration files containing sensitive data)
| System Maintenance | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
SEC-36 | DERMS shall employ cryptographic best practices such as encryption key management protocols and Key rotation
SEC-37 | DERMS shall integrate with infrastructure monitoring services to alert on resource usage thresholds
SEC-38 | DERMS shall support hot patching without interrupting system functions
SEC-39 | DERMS shall provide and maintain documentation that covers all product features and keep it current with shipped releases
SEC-40 | Specify if your system is SOC1 or SOC 2

## Data Access
ID | Requirement | Use Case Description | Vendor Response Section
| Data Management |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
DA-1 | DERMS shall interface and integrate with external data historian, receiving data and modifying data in data historian as needed | EM&V activities require DSM program data to be pulled from data historian; all DERMS data should be available in data historian as well
DA-2 | DERMS shall allow the retrieval of data remotely via web services | To support reporting requirements for all stakeholders
DA-3 | DERMS shall allow the retrieval of data via an ad hoc query, specifying time and date of interval | To support reporting requirements for all stakeholders
DA-4 | DERMS shall allow data retention to be configured per customer need | To comply with data retention policies
DA-5 | DERMS shall support API integration | External systems are required to interact with DERMS, some of which may only have API integration capabilities
DA-6 | DERMS shall import CSV and XML files to configure new or modify existing assets, sites, customers etc. | This data field tracks DER interconnection requirements

## Optimization
ID | Requirement | Use Case Description | Vendor Response Section
| Optimization |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
OPT-1 | DERMS shall allow events to be triggered by an external system (i.e. ADMS, Market, etc.) | DER controls as a result of ADMS grid support requests
OPT-2 | DERMS shall provide feedback to external systems on impact of control | Ensures FTM DER assets are controlled as expected when called upon
OPT-3 | DERMS shall optimize individual assets for economic objectives | In support of economic dispatch
OPT-4 | DERMS shall optimize all assets at an individual meter / site for economic objectives | In support of managing customer usage
OPT-5 | DERMS shall manage optimization within an event (compensation for non-performing DERs) | In support of DSM and distribution grid service programs, ensuring aggregate targets are met
OPT-6 | DERMS shall display optimization changes within an event (compensation for non-performing DERs) | In support of DSM and distribution grid service programs, ensuring aggregate targets are met
OPT-7 | DERMS shall optimize assets withing an asset group against a Time of Use rate structure | In support of SDCP planning
OPT-8 | DERMS shall optimize assets at a customer location against a Time of Use rate structure | In support of SDCP customer programs

## Monitoring
ID | Requirement | Use Case Descriptions | Vendor Response Section
| Real-time monitoring |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
MON-1 | DERMS shall monitor individual DER asset production in real-time (i.e. solar production smoothing/capacity firming, intermittent generation ramp rate control) | Visualization of real-time production by location helps inform distribution operation decisions
MON-2 | DERMS shall monitor real-time load drop by asset or group in a single event window | Validates that control actions from DERMS are working as expected
MON-3 | DERMS shall monitor real-time dispatch or charging of a storage system | FTM battery storage dispatched to charge or discharge for distribution system support
MON-4 | DERMS shall monitor assets online and offline status (thermostat, water heater, solar site, battery, DG) | Identifies for DSM program managers when participants are offline and not participating
MON-5 | DERMS shall monitor current utilization of EV charging infrastructure | EV charging infrastructure pilots need utilization info to inform long term program decisions
MON-6 | DERMS shall monitor current utilization of EV batteries through telematics | EV charging infrastructure pilots need utilization info to inform long term program decisions
MON-7 | DERMS shall monitor DER asset health (i.e. voltage, temperature, state of health, visual alarms, fire detection, failure diagnosis) | FTM DER asset health monitoring
MON-8 | DERMS shall monitor islanding and resiliency (remote disconnect or local response) status | FTM DER assets may operate in islanding or resiliency modes, DERMS must be aware of when this occurs
MON-9 | DERMS shall provide real-time monitoring of asset Volt/VAR support i.e. status of adjustments at inverter | FTM battery storage providing voltage support on distribution shall be tracked in real-time
MON-10 | DERMS shall provide real-time monitoring of asset or aggregate load following (as VPP or as local load) | In support of FTM DER control for grid support
MON-11 | DERMS shall provide real-time monitoring storage flexibility and availability | Distribution operators must know what to expect at time of dispatch for emergency operations
MON-12 | DERMS shall provide real-time monitoring of asset or aggregate participation in congestion relief | Distribution operators must know real-time operations when DERs are dispatched to provide grid support
MON-13 | DERMS shall report the total resource capacity available based on configured groupings (i.e. LMP nodes or substations) | Distribution and Market operators must know what to expect if DERs are dispatched to provide grid support or participate in markets.
MON-14 | DERMS shall track DER performance against control signals | Operators must know if DERs are performing as expected in both real-time and post-event
MON-15 | DERMS shall identify telemetry failures and issue an alarm in the case of such failure | When DERs are used for grid support, operators must know when DERs are unavailable for dispatch. Alarm notifications allow time for telemetry failure to be corrected.
MON-16 | DERMS shall indicate when a control action is in progress | Allows operations groups to know when DER resources are unavailable due to dispatch
MON-17 | DERMS shall have the capability to verify that control actions are received by assets | DERs may respond to control signals with an acknowledgment of participation, DERMS shall indicate as such
MON-18 | DERMS shall show a user how much contracted load is available across all assets | Real-time availability allows operations to make informed decisions
MON-19 | DERMS shall support real-time connection and visibility to Distributed Generator (DG) assets | In support of DG asset health monitoring
MON-20 | DERMS shall log user-specified control actions for post-event evaluation | Allows post event evaluation and auditing
MON-21 | DERMS shall perform real-time contingency analysis | Ensures dispatch targets are met during DR and DER events
| Asset Health Management and Monitoring |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
MON-22 | DERMS shall support monitoring of 3rd party data to monitor connectivity and asset health | Monitoring of utility-owned FTM DERs to notify operations when health-related issues arise
MON-23 | DERMS shall support tracking of alarms with reason codes for solar, storage, generators | Monitoring of customer / aggregator - owned FTM DERs to notify operations when health-related issues arise
MON-24 | DERMS shall track storage depth of discharge, number of cycles, and round trip efficiency for individual storage assets | FTM battery storage data monitoring points
MON-25 | DERMS shall record all control malfunctions | Control message failures should be tracked to support operations groups and post-event evaluations

## Forecasting
ID | Requirement | Use Case Descriptions | Vendor Response Section
| Forecasting |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
FOR-1 | DERMS shall allow the creation of custom forecasting models | Forecast methodology should be configurable to support grid operation needs
FOR-2 | DERMS shall allow for weather inputs for DER production forecasting | To enhance solar production forecasts, as well as inform future flexibility forecasts based on weather conditions impacts on previous events
FOR-3 | DERMS shall allow for simulation of events for planning or event management purposes | In support of planning, simulated events allow planners and operators to see grid impacts from DER operations
FOR-4 | DERMS shall calculate solar forecasts | Solar production forecast based on weather forecasts allows distribution operators to identify potential grid issues.
FOR-5 | DERMS shall calculate operational forecasts for expected DR capabilities | Forecasts allow operations teams to make informed decisions
FOR-6 | DERMS shall support dynamic forecasting (assets participating in other programs, forecast updates, non-communicating assets) | Assets may be enrolled in multiple programs for markets and distribution services, dynamically updated forecasts ensure operations have up-to-date program impacts
FOR-7 | DERMS shall consider offline assets when determining real-time flexibility | Offline assets are not available to dispatch, dynamically updated forecasts ensure operations have up-to-date program impacts
FOR-8 | DERMS shall create and export supply and demand profiles by DER resource | In support of planning efforts
FOR-9 | DERMS shall account for performance on similar days when creating forecasts | Past performance based on time, season, weather etc. shall be considered to refine future forecasts

## Visualization
ID | Requirement | Use Case Description | Vendor Response Section
| System Administration |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
VIZ-1 | DERMS shall support user role based access around programs and their associated data | This data field supports DER advanced inverter functionality
VIZ-2 | The DERMS Operational User Interface shall include and display dynamic real-time information and static (non-updating) information about selected DER assets. | DERMS users to have a singular view into the DERs on the system
VIZ-3 | DERMS shall support user role definitions that define permissions for each user type i.e. Information and control access, data review/edit capabilities | Based on code of conduct rules, certain business units shall not have visibility to specific data (i.e. Market Operations cannot see individual customer data)
| User Interface and Display Capabilities |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
VIZ-4 | DERMS shall provide a centralized platform/dashboard to monitor DER portfolio FTM and BTM | DER monitoring informs distribution operation and planning decisions
VIZ-5 | DERMS shall show real-time production of individual and aggregated assets from a single screen | Visualization of real-time production by location helps inform distribution operation decisions
VIZ-6 | DERMS operator shall view total asset inventory list for dispatch or monitoring from a single display screen | This visualization supports real-time monitoring by operations groups and quick access for dispatch as needed
VIZ-7 | DERMS shall display the forecast, monitor, and control individual and aggregated assets from a single screen | In support of increased operator efficiency
VIZ-8 | DERMS shall allow user to access a visualization of DER generation over time | DER production trends over time inform planning studies and operations decisions
VIZ-9 | DERMS dashboard shall display locational view of DERs on the system | Visualization of real-time production by location helps inform distribution operation decisions
VIZ-10 | DERMS dashboard shall display DER asset online/offline status | Utility-owned aAssets require monitoring and insight when communication to DERMS is lost
VIZ-11 | DERMS shall see previously scheduled, pending, and canceled events from the UI | Provides insight to operations teams of pending and active events
VIZ-12 | DERMS shall control different asset types from one screen | In support of increased operator efficiency
VIZ-13 | DERMS shall provide display alerts for issues regarding assets | In support of operator asset health needs and notification
VIZ-14 | DERMS shall configure custom fields in the UI for DERs or other assets or customer or group data | Custom fields may be used to track and group customers for control

## Control
ID | Requirement | Use Case Description | Vendor Response Section
| Controls |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
CON-1 | DERMS shall manage asset control for:
| Peak Shaving | Economic dispatch
| Peak Shifting | Economic dispatch
| Market Signals | Market dispatch
| Inverter set-point controls | DER controls as a result of ADMS grid support requests
| Pre charging (storage) | DSM program operation for battery storage
| pre-cooling thermostats | DSM program operation for thermostats
| degree offset for thermostat control | DSM program operation for thermostats
| Water heater pre-heating | DSM program operation for water heaters
| V2G | EV program evaluation
| EV charger curtailment | DSM program operation for EV charging
| Generator start up | DSM program for distributed generation
CON-2 | DERMS shall have the ability to send set-point control commands to individual and aggregated DER assets | In support of market dispatch and DER control as a result of ADMS grid support requests
CON-3 | DERMS shall perform load flexibility dispatch (reducing or increasing) | DER controls as a result of ADMS grid support requests
CON-4 | DERMS shall have the ability to dispatch all DERs for emergency | DER controls as a result of ADMS grid support requests
CON-5 | DERMS shall have 2-way communication to see event opt outs | In support of DSM program management
CON-6 | DERMS shall support localized TOU or Dynamic Pricing | In support of potential future DSM or commercial EV charging programs
CON-7 | DERMS shall be able to dispatch multiple programs simultaneously regardless of program type | Economic, market and emergency dispatch of DSM programs may run simultaneously to distribution system programs
CON-8 | DERMS shall manage device characteristics/limits based on interconnection or program rules, including DER over-generation | Characteristics include DER export limits and operating modes. In support of DER interconnection rule management
CON-9 | DERMS shall be able to remove assets that are already being used for another event from the available assets to be dispatched | Economic, market and emergency dispatch of DSM programs may run simultaneously to distribution system programs. Assets enrolled in multiple programs must have flexibility to prioritize which programs to participate in when called by multiple programs
CON-10 | DERMS shall support demand response for FTM DER assets | In support of DR programs dispatched by Market Operations
CON-11 | DERMS shall support demand response for BTM DER assets | In support of DR programs dispatched by Market Operations
CON-12 | DERMS shall provide control for islanding/resiliency (remote disconnect or local response) event response | FTM DER assets may require islanding or disconnection from grid during restoration efforts
CON-13 | DERMS shall support solar smoothing/capacity firming (i.e. ramp-rate control) | DER controls as a result of ADMS grid support requests
CON-14 | DERMS shall have the capability to send out event notifications based on distribution lists and event parameters | Notifications should be configurable to be sent out during different stages of the event lifecycle based on program rules.
CON-15 | DERMS shall create and save event templates for planned and unplanned events | Increase efficiency in operations groups if typical event configurations can be saved as a template
CON-16 | DERMS shall enable the scheduling of events ahead of time | In support of economic and market dispatch and scheduled DER operation
CON-17 | DERMS shall enable the scheduling events with no lead time | In support of emergency operation
CON-18 | DERMS shall allow for the cancellation of an event | Provides event flexibility when conditions change that require events to be canceled
CON-19 | DERMS shall notify a utility user if an asset or program is not able to be called based on constraints | In support of preventing groups from causing program constraint violations
CON-20 | DERMS shall notify if updates or modifications are done to the event | Provides event flexibility when conditions change that require events to be modified
CON-21 | DERMS shall allow for verification that events are successfully sent to and executed by assets | Ensures FTM DER assets are controlled as expected when called upon
CON-22 | DERMS shall track and send schedules to individual DERs and groups | DER controls as a result of ADMS grid support requests or TOU and Pricing program schedules
CON-23 | DERMS shall override configured asset constraints in emergency scenarios | Assets enrolled in multiple programs must have flexibility to prioritize which programs to participate in when called by multiple programs
CON-24 | DERMS shall have ability to aggregate assets in real-time to adhere to certain market conditions | In support of market participation
CON-25 | DERMS shall automatically dispatch assets based on market conditions | In support of market participation
CON-26 | DERMS shall enable and disable devices to bring them on and offline | FTM DER assets may require islanding or disconnection from grid during restoration efforts or for resiliency purposes
CON-27 | DERMS shall be able to switch individual or aggregated DERs from remote control to local control | FTM DER assets may be required to operate under local control during restoration efforts or for resiliency purposes
CON-28 | DERMS shall direct storage devices to charge or discharge based on conditional rule sets (i.e. begin charging if state-of-charge is less than 20%) | DER controls as a result of ADMS grid support requests
CON-29 | DERMS shall download schedules to individual or aggregated DERs i.e. schedule information to include charge and discharge start and stop times, power factor, and energy | In support of EV charging management and FTM battery storage operation
CON-30 | DERMS shall enforce preset limits based on interconnection requirements (i.e. real and reactive power input and output) | In support of interconnection agreement limit enforcement and tracking in real-time
CON-31 | DERMS shall adjust inverter settings (i.e. VAR, volt-amp, inverter modes, volt/VAR curve setpoints, voltage dead band, maximum watts, etc.) | DER controls as a result of ADMS grid support requests
CON-32 | DERMS shall invoke control modes through a direct request to an individual or aggregated group of DERs | DER controls as a result of ADMS grid support requests
CON-33 | DERMS shall randomize and stagger return to normal operation to prevent large changes in demand | To prevent a demand "snapback" upon return to normal operation
CON-34 | DERMS shall detect communication failures and take suitable actions following the detection of a communication failure (i.e. retrying communication action or producing an alarm) | Monitoring of utility-owned FTM DERs that participate in distribution grid support to notify operations when health-related issues arise
CON-35 | DERMS shall send power set-points and objectives to the DER controller such as real and reactive power, voltage, etc. | DER controls as a result of ADMS grid support requests
CON-36 | DERMS shall receive event dispatch signals from the utility energy supply team | In support of dispatch
CON-37 | DERMS shall send real-time DSM program availability to the utility energy supply team | In support of dispatch

## Program Management
ID | Requirement | Use Case Description | Vendor Response Section
| Programs |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
P-1 | DERMS shall support the management of Residential programs and DER assets (EV chargers, BTM batteries, thermostats, load switches, water heaters, etc.) | In support of Residential Customer Programs
P-2 | DERMS shall support the management of Commercial and Industrial programs and DER assets (large BTM solar, storage, DG, fleet management etc.) | In support of Commercial and Industrial Customer Programs
P-3 | DERMS shall support the creation of programs for both DER and DR assets at an individual asset level | In support of DSM programs and FERC 2222 implementation
P-4 | DERMS shall support the creation of programs for both DER and DR assets at an aggregated asset level | In support of DSM programs and FERC 2222 implementation
P-5 | DERMS shall allow the importing of enrollment data from utility systems | Enrollment data will flow from utility systems into DERMS
P-6 | DERMS shall allow the importing of enrollment data from third-party utility service providers / program implementer systems | Enrollment data will flow from 3rd party program admin head-ends into DERMS
P-7 | DERMS shall support the dynamic enrollment of assets within programs | Enrollment data will automatically update from 3rd party program admin head-ends into DERMS
P-8 | DERMS shall support multiple program participation of an asset in accordance with applicable program constraints | Allows assets to participate in both retail and wholesale level market programs.
P-9 | DERMS shall have the capability to send and receive enrollment information or asset grouping information from other systems on a scheduled or ad-hoc basis | In support of changing locational information (i.e. switching info to update circuits from ADMS), and updated program enrollment info from 3rd party program admins
P-10 | DERMS shall manage a 3rd party aggregator's individual assets enrolled in utility programs | In support of DSM programs and FERC 2222 implementation

## Constraint Management
ID | Requirement | Use Case Description | Vendor Response Section
| Program Constraint Management |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
CM-1 | DERMS shall have a configurable calendar to define holidays, weekends, and other program constraints | DSM programs typically include constraints that do not allow operation during certain day-types (i.e. holidays, weekends). Ensure dispatch f programs follow existing utility requirements.
CM-2 | DERMS shall limit the number of times a program can be called per week, month, year, season | DSM programs have finite events that cannot be exceeded per program rules.
CM-3 | DERMS shall have configurable constraints around the day of the week and daily event times a program is called | Some DSM programs include constraints that do not allow operation during certain hours of the day.
CM-4 | DERMS shall manage customer opt-out limits based on program rules | DSM programs require opt out tracking for incentive eligibility
CM-5 | DERMS shall create event priorities based on user role | When assets are enrolled in multiple programs, higher priority needs based on user roles initiating events will take precedence
CM-6 | DERMS shall allow for use case and program operational prioritization (example: reliability vs economic dispatch) | When assets are enrolled in multiple programs, higher priority programs will take precedence

## Communication
ID | Requirement | Use Case Description | Vendor Response Section
| Communication |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
COM-1 | DERMS shall support Sunspec Modbus | Communication protocol in support of IEEE 1547-2018
COM-2 | DERMS shall support OCPP 1.6 for EVSE | Standard protocol for EVSE
COM-3 | DERMS shall support OpenADR 2.0b | Widely adopted industry standard DR protocol
COM-4 | DERMS shall support DNP3 | SCADA communication for FTM DER and ADMS connection
COM-5 | DERMS shall support IEEE 2030.5 | DER-specific communication protocol that supports advanced DR and DER programs and control
COM-6 | DERMS shall support: ISO 15118 for V2G | Vehicle to grid communication interface to support bi-directional EV charging and discharging
COM-7 | DERMS shall support IEC 60870-6/TASE.2 (ICCP) | SCADA communication for FTM DER and ADMS connection
COM-8 | DERMS shall support the functional and interoperability requirements of IEEE 1547-2018 | Industry standard requirements for DER capability, including voltage and frequency regulation, and communication and monitoring capabilities
COM-9 | DERMS shall support Voice/Text/email notification of events to internal utility teams and customers | In support of notification requirements from DSM programs
COM-10 | DERMS shall support Voice/Text/email notification of events to DR and DER aggregators | In support of notification requirements from DSM programs
COM-11 | DERMS shall support email notifications to internal utility resources during a dispatch event lifecycle | Separate from external notifications, internal notifications are configurable for specific internal parties based on the DSM event lifecycle
COM-12 | DERMS shall support email notifications to internal utility resources in the event the system goes down or communication to external systems fails | In support of system maintenance
COM-13 | DERMS shall support 2-way communication for event participation acceptance from notifications | DSM programs require customers to opt out of events via phone call
COM-14 | DERMS shall allow users to opt-out from events using the response to email or voice messages | DSM programs require customers to have opt-out capability
COM-15 | DERMS shall allow users to create notification templates | Unique messaging is required per each DSM program
COM-16 | DERMS shall support CTA-2045 | In support of requirements from DSM programs

## Reporting & Settlement
ID | Requirement | Use Case Description | Vendor Response Section
| Billing |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
REP-1 | DERMS shall use meter data to track and assess DER generation, energy and power delivered and received i.e. multiple channels on net meter | In support of FTM and BTM DER participating in distribution system services
REP-2 | DERMS shall support incentive tracking (performance based, capacity) | In support of DSM program participation, incentives should be tracked and reportable
REP-3 | DERMS shall have the capability to generate settlement values | In support of program participation settlement or market settlement from expected vs actual delivery.
| Reporting |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
REP-4 | DERMS shall have pre-built core reports | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-5 | DERMS shall have integration to a 3rd party reporting tool for out-of-the-box and ad hoc reporting | To support reporting requirements for all stakeholders
REP-6 | DERMS shall export reports from the UI | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-7 | DERMS shall run reports on a schedule | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-8 | DERMS shall have reports with graphical as well as tabular components | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-9 | DERMS shall provide a way for users to assess the overall program statistics and performance for financial valuation of a program | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-10 | DERMS shall have the ability to track RECs - kWh produced by solar system. | In support of REC tracking
REP-11 | DERMS shall allow for the user to generate customized ad hoc reports. | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-12 | DERMS shall allow a user to compare meter data vs. asset telemetry data | Comparison of device level data against meter data to support EM&V activities
REP-13 | DERMS shall report individual assets vs. total event data | Event reporting for program tracking and regulatory reporting
REP-14 | DERMS shall track and store performance calculation values from asset and aggregate event performance | Event performance reporting for program tracking and regulatory reporting
REP-15 | DERMS shall allow auditing of asset performance | In support of program EM&V activities
REP-16 | DERMS shall report historical forecast values | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-17 | DERMS shall generate reports of inverter setpoints for all assets and allow user to view in report format | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-18 | DERMS shall report historical alarms with reason codes for solar, storage, and generators | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-19 | DERMS shall have reports that display asset inventory sortable by program, asset type, location etc. | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-20 | DERMS shall support reporting of cycling count and tracking | Asset health tracking for FTM battery storage assets
REP-21 | DERMS shall support reporting of individual and aggregation performance | In support of program reporting for EM&V, regulatory reporting and planning activities
REP-22 | DERMS shall track performance against defined schedules | In support of program reporting for EM&V, regulatory reporting and planning activities
| Baselining |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
REP-23 | DERMS shall have pre-defined core baselines. Please list the pre-defined baselines in your system. | DSM program evaluation requires baselines to evaluate program performance
REP-24 | DERMS shall allow for the creation of custom baselines within your system | DSM program evaluation requires baselines to evaluate program performance
REP-25 | DERMS shall import usable baseline models | DSM program evaluation requires baselines to evaluate program performance
REP-26 | DERMS shall create custom baselines for individual assets as well as aggregated | DSM program evaluation requires baselines to evaluate program performance
REP-27 | DERMS shall assign baselines to individual programs in the system | Different programs may utilize different baseline methodology
REP-28 | DERMS shall show multiple baseline models at one time for comparative purposes | In support of planning activities
REP-29 | DERMS shall continuously update baselines based on asset health and performance | DSM program evaluation requires baselines to evaluate program performance
REP-30 | DERMS shall automatically update baselines based on previous event information | DSM program evaluation requires baselines to evaluate program performance

## Markets
ID | Requirement | Use Case Description | Vendor Response Section
| Markets |  | Current Product | On Vendor Roadmap | Custom Development Required | Not in Scope | Additional Information
MKT-1 | DERMS shall support day ahead and real-time market bidding | In support of utility market participation
MKT-2 | DERMS shall support participation in the capacity / emergency curtailment market | In support of utility market participation
MKT-3 | DERMS shall support participation in the energy / locational marginal price (LMP) market | In support of utility market participation
MKT-4 | DERMS shall support participation in the ancillary services market | In support of utility market participation
MKT-5 | DERMS shall manage aggregations of assets for markets | In support of utility market participation
MKT-6 | DERMS shall track market participation at the asset level | In support of upcoming FERC 2222 allowance of DER market participation
MKT-7 | DERMS shall track market participation at the aggregation level | In support of upcoming FERC 2222 allowance of DER market participation
MKT-8 | DERMS shall calculate settlement for programs | In support of utility market participation
MKT-9 | DERMS shall support utility customers bidding into retail markets | In support of utility market participation
MKT-10 | DERMS shall support obtaining and managing aggregators' information on day-ahead and real-time bidding into retail markets | In support of upcoming FERC 2222 allowance of DER market participation
MKT-11 | DERMS shall have the capability to receive direct market dispatch signals from the wholesale market | In support of utility market participation with FERC 2222
MKT-12 | DERMS shall have the capability to override or cancel wholesale market DER dispatch on a day-ahead and real-time basis | In support of utility market participation with FERC 2222, preventing localized grid issues as a result of DER market participation
MKT-13 | DERMS shall support the California PUC implementation of the Market Informed Demand Automation Server (MIDAS) application and API for access to Real-Time pricing information | In support of real-time pricing applications and market signals